735 Guideform Specifications - OBSOLETE

March 26, 2002

Feeder protection shall be provided using a single static drawout relay. Protection features shall include:

- Three phase (51) and ground (51G) time overcurrent

- Three phase (50) and ground(50G) instantaneous overcurrent

- Independent phase and ground curves; ANSI, IAC or IEC/BS142 curve shapes: definite time, moderately inverse, normal inverse, very inverse, extremely inverse

- 40 “time dials” for phase and ground time overcurrent curves

- Separate pickup level and output relay for each protection element

- Three outputs: trip, auxiliary trip, and service

- Eight additional output relays shall be an option, one for each protection element

- Trip record: display of last five trips

- 86 lockout available

The relay shall have front panel LED indicators for:

- Cause of trip, pickup, relay in service, relay malfunction

A clear key shall be available to clear the cause of trip indicators.

A phase current indicator will be provided on the front panel.

The relay shall be able to communicate  via an RS485 port using the ModBus® RTU protocol. Communication software shall be provided.

The information available over this port shall include:

- Settings, phase and ground current as a % of CT, status

- Simulation of trips

The relay shall comply with surge withstand capability (SWC) standards such as ANSI C37.90 and IEC 255.4.