DIAC/DIFC/DSFC Guideform Specifications

April 09, 2002

Feeder protection shall be provided using digital microprocessor, self-powered, single phase relays. Protection features shall include:

- instantaneous overcurrent (50 or 50G)

- time overcurrent (51 or 51G)

- independent TOC and IOC pickup and timing settings

- 16 selectable TOC curves meeting GE, IEEE, and IEC standards

- latched targets for IOC and TOC which operate on trip circuit current

The reset characteristic can be selected to either emulate an induction disk or fast reset. The system frequency can be selected to be 50 or 60 Hz.

Two trip circuit test levers shall be located on the front panel. An LED pickup indicator shall be located on the front panel.

All settings shall be visible through the unit’s cover. Targets may be reset without removing the cover.

The relay shall be available as a complete drawout case and cradle assembly.