T60 – Guide form Specification

Firmware revision 7.60

Specification for Transformer Protection, Control and Monitoring

Comprehensive transformer protection, control and monitoring shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be applicable to medium and large transformers with up to six windings/restraints.

# Protection Functions:

## Biased Differential Protection

- Automatic ratio and vector group compensations shall be included.

- The protection shall be based on dual breakpoint, dual slope differential/restraint characteristic using maximum winding current for restraint.

- The element shall include built-in magnetizing inrush and overexcitation inhibits. The magnetizing inrush inhibit feature shall provide choice for per-phase, cross-phase, 2-out-of-3 or average blocking. The magnetizing inrush inhibit feature shall also provide choice for standard or adaptive restraint. The over excitation inhibit shall be on a per phase basis.

- The element shall include built-in CT saturation detection in order to maintain sensitivity while increasing security of the differential protection.

## Instantaneous Differential Protection

- The differential protection shall respond as an instantaneous overcurrent element on differential currents exceeding a settable pickup threshold overriding inhibits.

## Restricted Ground Fault Protection

- A minimum of 6 restricted ground fault protections (one per three phase and a ground CT bank) shall be provided.

- The protection shall respond to ground differential currents using single slope and maximum phase current for restraint.

## Overexcitation Protection

- Two volts-per-hertz elements shall be available upon voltage configuration. Each element shall respond to voltage/frequency ratio upon chosen source.

## Distance Protection

- Five phase and Five ground distance elements, directional/non-directional, each with a choice of quad or mho characteristic shall be available. Supervision of the distance elements shall be available by means of power swing detection and load encroachment element.

- As backup protection for transformers or adjacent lines.

## Thermal Overload Protection

# The relay shall have two elements for thermal overload protection.

- Elements have to be IEC255-8 compliant.

- The elements shall support thermal memory.

## Rate Of Change Of Frequency (ROCOF) Protection

Four ROCOF elements shall be available. Each element shall respond to a reference chosen source. Each element shall respond to rate of change of frequency with voltage, current and frequency supervision. Each element shall be able to be configured as Increase, Decrease or Absolute.

## Overcurrent Protection

- A minimum of twenty one  time overcurrent elements: phase, ground, neutral and negative phase sequence currents  shall be provided.

- Each element shall respond to either fundamental phasor magnitude or total waveform RMS magnitude upon chosen source.

- Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise or difficult coordination shall be available.

- A minimum of thirty nine  instantaneous overcurrent elements: phase, ground, neutral and negative phase sequence currents shall be provided.

- A minimum of nine directional overcurrent elements: for phase, neutral and negative-sequence (three elements for each) shall be available. Dual polarization modes which can be configured to prioritize on voltage or current polarization shall be available.

- Multiple voltage restrained overcurrent elements and upon chosen source shall be available.

- Sensitive ground over current element shall be available.

## Voltage Protection

- Three phase under voltage and three phase over voltage elements shall be provided.

- Each under voltage element shall respond to either phase to phase or phase to ground fundamental voltage signal and upon the chosen VT bank. A choice of inverse time or definite time shall be provided.

- Each over voltage element shall respond to either measured phase to phase voltage signal or derived from phase to ground voltage signal and upon the chosen VT bank. The over voltage elements shall be definite time dependent.

- Three auxiliary undervoltage and three overvoltage elements shall be provided per each voltage input of the relay.

- Three negative sequence overvoltage per each voltage input of the relay.

- Three neutral over voltage elements shall be provided. Each element shall be definite time dependent or a custom curve time dependent.

## Temperature Protection

- The relay shall support 8 programmable RTD inputs per RTD module

- The RTD shall supporting Ni100, Ni120, Cu10 or Pt100 RTD types.

- Each RTD input shall have two operational levels: alarm and trip.

- The element shall support RTD trip voting

- The RTDs shall provide open RTD failure supervision

- The relay shall also support a remote RTD module supporting 12 RTDs

# Control Functions

## Breaker Failure Elements

        - Six breaker fail elements shall be configurable to respond to two different currents such as in breaker-and-a-half application

        - The breaker fail element shall be applicable for 3 pole tripping or 3 pole / 1 pole tripping

        - The breaker fail shall have phase and neutral supervision elements

        - Breaker fail timers shall be supervised with a fast CB auxiliary contact and current elements or with current elements only or with a CB auxiliary contact only

## Synchro-check

        - Six synchrocheck elements shall be provided

        - The synchrocheck elements shall be configurable to respond to any combination of single-phase voltages.

        - The synchrocheck element shall monitor the difference in voltage magnitudes, phase angles and frequencies

        - The check synch element shall take account of the CB closing time

        - Live and Dead source logic shall be included.

- Breaker and Switch Control Elements

Six breaker control elements shall be provided to control the breaker operations.

Twenty four switch control elements shall be provided to control the switch operations

## Programmable logic including non-volatile latches

## Sixteen Elements for user-definable protection functions

Flexible control of all inputs and output contacts shall be provided.

All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

The relay shall allow for peer-to-peer communications direct fiber or G.703 or RS422 interfaces.

## Switchable Setting Groups

The relay shall have six switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

## FlexLogic programmable logic

- The relay shall have 1024 lines of user programmable logic with necessary Boolean logic and control operators to define custom schemes. Logic operators like AND, OR, NAND, NOR, NOT, XOR, Latch, Timer, Positive/Negative and dual One Shot must be supported. Non-volatile latches must also be available.

- Flexible control of all inputs and output contacts shall be provided.

## All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

# Metering and Monitoring Functions

## Metering

## Differential and Restraint Current

- Per-phase differential and restraint currents – magnitudes and angles, as well as per-phase differential 2nd and 5th harmonic levels (percent and angle)

## Voltage, Current, Power, and Energy

The following measured entities shall be available upon the chosen reference source:

- Voltage (phasors, true RMS values and symmetrical components, harmonics up to 25th). Current (phasors, symmetrical components, true RMS values and harmonics up to 25th). Power (real, reactive and apparent). Power factor. Demand, energy and frequency.

- Per-phase, per-source 2nd to 25th harmonic currents, and THD (Total Harmonic Distortion).

- Synchro-check data (delta voltage, delta angle and delta frequency)

- Frequency rate of change per each of the four elements.

## Phasor Measurement Unit (PMU)

- An optional phasor measurement unit (PMU) with 16 analogue inputs for power system monitoring, protection, operation, and control shall be available. The relay shall provide optional synchronized phasor information of voltage, current and sequence components according to the IEEEC37.118 and IEC61850-90-5 standards. The streaming rate shall be user programmable, should have an onboard memory, manual or user configurable trigger options. The relay shall be capable of streaming the Synchrophasors data over its Ethernet port. Metering “M” and Protection “P” class synchrophasors shall be supported.

## Monitoring

## Trip circuit monitoring

- To monitor the trip circuit continuously, independent of the breaker, a trip seal-in scheme to maintain the monitoring current flow through the trip circuit when the breaker is open shall be provided.

## VT Fuse Failure detection

- The relay must support a fuse failure detector element for raising an alarm and/or block elements that operate incorrectly for a full or partial loss of AC potential caused by one or more blown fuses. Some elements that can be blocked (via the BLOCK input) are distance, voltage restrained overcurrent, and directional current.

## CT Failure

- The relay must support a CT failure function for detecting problems with system current transformers used to supply current to the relay. This functionality must detect the presence of a zero-sequence current at the supervised source of current without a simultaneous zero sequence current at another source, zero-sequence voltage, or some protection element condition. Upon detection, pertaining operands must be available to block protection elements that could miss-operate due to the detected CT fail condition.

## Condition monitoring

- Hottest-spot temperature, top oil temperature, aging factor and loss-of-life and through fault i2t (including breaker flash over when in the open position) data as well as measurement of auxiliary voltage shall be available.

## Breaker Arcing Current (I2t)

- The relay shall calculate an estimate of the per phase wear on the breaker contacts by measuring and integrating the current squared passing through the breaker contact as an arc.

- Digital Fault Recorder (DFR)

The relay shall provide the following disturbance recording capability:

Oscillography (Transient Recorder): The relay shall have the capability to store raw sampled data with programmable sampling rate, up to 64 samples per cycle. The relay must also have provision for configurable oscillography records (up to 64), number of digital channels (up to 64), number of additional analog channels (up to 16), pre-trigger (0 to 100%), trigger command and recording mode.

The number of triggered oscillography records shall be available via communication.

Oscillography files must support IEEE C37.111-1999/2013, IEC 60255-24 Ed 2.0 COMTRADE standard

The oscillography memory shall allow for storing 3 consecutive records of 244s each.

Sequence of Event recorder (SOE) function with a capacity to store 1024 events with 1ms time stamping accuracy.

The relay shall have settings to compensate time change, and then always show the accurate time when installed in regions that change time during the year period.

The fault report shall store data, in non-volatile memory, pertinent to an event when triggered. The captured data contained in the FaultReport must include:

• Fault report number

• Name of the relay, programmed by the user

• Firmware revision of the relay

• Date and time of trigger

• Name of trigger (specific operand)

• Line or feeder ID via the name of a configured signal source

• Active setting group at the time of trigger

• Pre-fault current and voltage phasors

• Fault current and voltage phasors (one cycle after the trigger)

• Elements operated at the time of triggering

• Events - Nine before trigger and seven after trigger (only available via the relay web page)

• Fault duration times for each breaker (created by the breaker arcing current feature)

## Relay HMI

The relay shall provide the following user interface capabilities.

Graphical HMI

A 7” colour graphic display HMI option shall be available.

The graphical HMI must support dynamic single line diagrams with pre-configured and custom modes and controls.

The graphical HMI must also support the following screens: Annunciator panel with up to 96 cells, actual values screens, commands, targets and records.

The default page must be configurable, and can be set between rolling between pages or remain with default or go to screen with alarms.

The relay shall support the following pushbuttons:

5 Tab and 1 Home pushbutton for page recall

4 directional, 1 Enter and 1 Escape pushbutton element selection

10 Side pushbuttons for power system element control

Reset and Help pushbuttons

8 physical User-programmable pushbuttons

The relay shall support the following LEDs

5 device status indicators (In Service, Trouble, Test Mode, Trip, Alarm)

9 event cause indicators (Color configurable: Red, Green, Orange)

8 user-programmable pushbutton indicators

Standard HMI

Provisions for 48 user programmable LEDs and custom labeling capabilities

Provisions for 16 large user programmable pushbuttons to perform manual control, operate breakers, or lock-out functions and its operation shall be logged directly in the sequence of events recorder.

Users must be able to navigate and edit settings using the relay’s front panel.

The device shall also have dedicated-function LEDs for showing internal status.

The device and the configuration software shall support different languages: English, French, Russian, Chinese, German, Turkish, Japanese and Polish. A way for changing the relay language (Eg. configuration tool) in the field shall be provided.

The front panel enclosure protection shall be IP54 (graphical HMI)

## Settings

The relay has to support a method to protect the setting file. Users shall be able to choose the settings they want to protect and those they want to be unprotected. Protection should demand a password. The settings file shall stay protected when sent and opened on a different computer.

The relay must register date and time of setting file upload (setting file sent to the relay).

Relays with IEC61850 capabilities must be able to support SCL files (.ICD, .CID and .IID) for writing and reading to/from the relay. A setting file in this format can be directly sent or red from a 3rd party software using MMS file transfer service. For secure file transfer, SFTP must be available.

All required settings (logic, protection, communications, etc.) for the relay configuration must be part of a single setting file.

# Communications

## Networking options

The relay shall provide different networking options including:

- Three independent Ethernet ports (independent IP and MAC addresses) with fiber LC or copper RJ-45 pluggable connectors (SFP type), 100Mbps.

- RS485 rear port and RS232 front panel interface shall be available.

- IRIG-B input (TTL compatible)

- The relay shall also provide exchange of binary information with other devices of the same family over a dedicated multimode or single mode fiber. Redundant channels must be available.

- Other interfaces must be available: RS422, G.703 and IEEEC37.94 at 64/128kbps interface.

Two of the relay Ethernet ports have to support two redundancy techniques: Hot-standby and Parallel Redundancy Protocol (IEC62439-3 PRP 2nd edition - 2012). The redundancy method should be user-selectable via settings.

When PRP is selected, actual value of the following parameters must be available: counter for total messages received on port A and B; counter for total messages received with an error (bad port code, frame length too short) and counter for total messages received with an error on each port (A and B)

The relay shall support the following communication protocols: IEC 61850 Ed. 2, SFTP, MMS File Transfer Service, DNP 3.0 & Modbus Serial/TCP, IEEE 1588 – PTP and PP profiles, IEC 60870-5-104 and 103, SNTP, HTTP, TFTP and IEEE C37.118 for Synchrophasor data.

Simultaneous communication via multiple communication protocols (Eg. IEC61850, DNP 3.0 and Modbus) must be supported

The IEC61850 protocol shall include an extended implementation of logical nodes. All relevant P&C elements must be mapped to their respective logical node. All available data items and data attributes must be available to use for configurable GOOSE. GOOSE messages shall be fast enough to be published within 3 ms after data change.

GOOSE messages shall support configurable re-transmission profiles. At least four different profiles (slow to fast) shall be supported.

The relay shall be able to subscribe to up to sixteen (16) 61850 GOOSE publishers. Up to 32 data items shall be received from a single publisher.

The relay shall support routable GOOSE, R-GOOSE. This enables customer to send GOOSE messages beyond the substation, which enables Wide Area Protection & Control (WAPC) and more cost effective communication architectures for wide area applications. Any dataset shall be transportable via either GOOSE or R-GOOSE.

A total of 18 user-configurable data sets must be supported. 6 of them must be fast (2ms update rate) plus 12 standard datasets (100ms update rate). These data sets must be assignable to buffered (BRCB), un-buffered (URCB) or GOOSE (GCB) control blocks via settings. Assigning one data set to multiple control blocks must be supported. Each data set must be 64 data items long as a minimum. Data sets must support analog values.

The relay must support multiple-configurable logical devices, which means users can group available logical nodes into user-configurable logical devices. There must be 18 configurable logical devices available.

The relay must support simultaneous connection to up to five IEC61850 clients.

The relay clock shall be capable of being synchronized with an IRIG-B signal or via its Ethernet ports to allow time synchronism with other connected devices. The relay shall allow for IEEE 1588 “PTP or PP” network-based time synchronization.

The relay must support daylight saving compensation (local time), this allows for specifying the local time zone offset from UTC (Greenwich Mean Time) in hours

## 61850 Process Bus (Merging Unit)

The relay has to be able to work on differential schemes equipped with 61850 process bus. The relay shall support direct and dedicated connection to up to four merging units and shall be able to use all current, voltage, digital and any other data to feed the transformer differential scheme. Merging units substitute the relay’s AC and contact inputs / outputs. However, a contact input and output module shall be supported in parallel with the merging unit.

## Cyber Security

- Basic Security

The relay shall support at least three password-protected levels of access: one for Settings (allows users to modify setting files), one for Commands (allow users to execute operator commands) and restricted (see only mode). Relay passwords shall support alpha numeric and special characters, capital and low case letters.

The relay shall support independent local and remote passwords for each access level. Local passwords are needed for working through the front panel and front communication port. Remote passwords are needed for working through the rear comm ports (serial or Ethernet)

The relay shall allow users to configure what actions to take when unsuccessful password access attempts are made. Users shall have the ability to configure how many unsuccessful attempts are made before users are locked out of the device, as well as have the ability to configure how long users will be locked out from re-entering the password once this limit is reached.

Successful attempts to enter any passwords into the relay shall be recorded in the Event Record.

The relay shall have security measures to ensure explicit permission is granted from the controlling authority. This way a second person is required to grant access to the relay even when a user knows the proper password.

The security measures shall ensure that, before a user can make any changes to the relay settings, the local / remote operator must first ‘surrender’ the relay to grant the user the ability to make changes to the settings.

Eg. When the remote operator ‘surrenders’ the relay, the local operator is required to enter a ‘Setting Level’ password before making any changes to the relay.

A security audit trail of elements must be supported. This element must capture setting changes, Log-in/out related events and information on the computer where those changes came from.

- Enhanced Security (optional)

The relay must support 5 access roles (Administrator, Supervisor, Engineer, Operator and Observer) with independent passwords. Authentication must be available at the device level (passwords stored locally in the relay) and at the server level via Radius (users, credentials and passwords managed from a Radius Server). Communication between the Radius Server and the relay must be secured (Radius over TLS).

Communication between the relay and the configuration software must also be secured (Modbus over SSH tunnel).

The supervisor role (when enabled) must have the rights to log-off and/or authorize access to other roles. Eg. a user with engineer rights will be able to log-in only when another user with supervisor rights enables access.

Password complexity must meet NERC-CIP-5 requirements (minimum 8 characters, three or more different types of characters - uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric).

The relay must provide security event reporting through the Syslog protocol for supporting Security Information Event Management (SIEM) systems and centralized cyber security monitoring. This must be stored in the device non-volatile memory and be segregated from the main event recorder.

There must be multiple security by-pass modes (local, remote, push button) that allows for reduced security when testing the relay.

The relay must produce a security audit trail that shows changes to the settings and provide details as IP and MAC address of the computer used for doing the changes

The relay must have a mechanism to reset all user content in it (default the relay to factory settings/records). This mechanism also resets all passwords. This command must only be available via the relay front panel.

An authentication bypass setting must be provided for ease of access when performing lab tests.

Authentication bypass must also be available for pushbuttons only, for those cases where operators are not required password for command such “acknowledge” or “emergency trip”

End users must have the capability of disabling any Ethernet port when not is used. Settings for this purpose must be available.

# General Requirements

## Digital I/O

The relay’s contact inputs shall accept wet or dry contacts.

Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. H Standard contact output for tripping must operate in <4mili seconds. Fast solid-state contact outputs with operating time of <0,1 mili seconds must also be available.

Hardware input/output capability shall be expandable up to a maximum of 120/72 digital I/O.

The relay shall support double-point status logic for Breakers and Isolators.

The relay shall support 4 voltage thresholds (17V, 33V, 84V,166V) for the digital inputs.

## Toolsuite

The relay shall be supplied with supporting application software for use on a PC with Windows® operating systems. The program shall be capable of retrieving COMTRADE oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay

The relay shall have setting software with advance settings tool to allow easy configuration of IEC61850 GOOSE messages.

The software shall allow customers group settings files by location/substation (subfolders).

The software shall be able to compare settings files and show discrepancies.

The software shall be validated for running on windows XP, windows vista and windows 7 and windows server 2008.

## Relay Monitoring

The relay shall monitor internal temperature and generate an alarm when the temperature levels get close to the relays operating limits.

The relay shall monitor internal DC auxiliary voltage levels and generate an alarm when detecting an over or under voltage condition. This enable users to schedule preventive service to the relay before it fails

## Mounting

The relay shall be available in either 19” rack horizontal mounting or reduced vertical option. Mounting accessories shall enable the relay’s front panel to be installed separate front the relay’s chassis. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules.

## Preference

Manufacturer: GE Multilin

Device Number and Name: T60, Transformer protection system