269 Plus Guideform Specifications

March 26, 2002

Motor protection and management shall be provided by a digital relay.

Protective functions shall include:

- phase overload standard curves (51)

- overload by custom programmable curve (51)

- I2t modeling (49)

- stator overtemperature/bearing overtemperature with 10 independent RTD inputs (49)

- negative sequence unbalance/ single phase (46)

- phase reversal (47)

- starts per hour and time between starts (48)

- short circuit (50)

- ground fault (50G/50N/51 G/51 N)

- undercurrent (37)

- mechanical jam/stall

Management functions shall include:

- statistical data

- pre-trip data

- ability to learn, display and integrate critical parameters to maximize motor protection

- communication with external devices using a RS485 port and ModBus® RTU protocol

- a keypad and 48 character LCD display

A metering option shall be available as a separate unit that communicates with the relay which may be field installed without modification to the relay. The metering option can be used with any relay where diagnosis or load measurements are required and shall also provide isolated analog outputs for average RMS amps, kW, kvar and PF.

With the meter option, the relay shall be capable of displaying important metering functions, including phase voltages, kilowatt, kilovar, power factor, frequency and MWhr. In addition undervoltage (27) and low power factor alarm and trip levels shall be field programmable.