369 Guideform Specifications

September 2006

NOTE TO SPECIFIER:

For more information on this product visit the GE Multilin Web Site for a product brochure and instruction manual at

http://www.geindustrial.com/products/brochures/369.pdf

http://www.geindustrial.com/multilin/manuals/369.htm

The motor management relay shall provide primary protection and management to medium voltage motors.   The relay shall be equipped with the following protection functions.

- Motor Thermal Overload Model (49)

  - Include 15 standard overload curves, a custom curve feature, and a curve specifically designed for the starting of high inertia loads, when the acceleration time exceeds the safe stall time.

  - The stator protective thermal model shall combine inputs from phase and unbalance currents, and RTD winding feedback. This will then cause the model to become dynamic in nature in order to follow the loading and temperature of the motor.

  - Motor cooling time constants

  - Rotor protection during stall and acceleration. To achieve this a speed switch input shall be available.

- The relay shall detect ground faults or earth leakage currents as low as 0.25 A using a 50:0.025 Ground CT.

- Use phase and unbalance current heating to calculate motor thermal capacity during starting and running states

- Settable motor stopped and motor running cooling time constants

- Phase and residual overcurrent elements (50P/50G)

- Unbalance / single phase biasing (46)

- Load-loss (undercurrent) (37)

- Mechanical jam (48)

- Motor stall protection

- Re-start blocking timer to be used as a start permissive to ensure the motor had slowed to a safe speed or to a complete stop, before it can be re-started again

- Antibackspin protection ensuring that the motor can only be re-started when it has slowed to within acceptable limits.  A backspin detection voltage input shall be provided to measure frequency.  If the measured frequency is below a programmed minimum threshold, the backspin start inhibit shall be removed

- Starts-per-hour (66)

- Minimum-time-between-starts

- The relay shall provide an option for voltage transformer inputs, which shall be used to provide overvoltage (59), undervoltage (27), voltage phase reversal (47), overfrequency (81O) and underfrequency (81U) functions

- The relay shall be equipped with an Undervoltage Auto-restart function that will restart the motor after an undervoltage trip caused by a momentary loss of power.

- 12 RTD inputs with associated over-temperature protection functions including alarm and trip settings, with corresponding settable time delays, and associated outputs.  The following additional functionality shall be provided, associated to RTDs:

  - Able to configure each of the twelve RTDs as “None” or any one of four application types: “Stator”, “Bearing”, “Ambient”, or “Other”

  - RTD type shall be selectable between four different RTD types: “100 Ohm Platinum”, “120 Ohm Nickel”, “100 Ohm Nickel”, or “10 Ohm Copper”

  - The motor relay shall incorporate the RTD inputs to support the following:

    - Thermal overload model biasing

    - Temperature alarms and trips (49/38)

    - RTD open- or short-circuit alarm

  - The motor relay shall include trip voting for extra reliability in the event of RTD malfunction.  If enabled, a second RTD must also exceed the trip temperature of the RTD being checked before a trip is issued

  - Provisions shall be included to allow the RTDs to be identified by name

- The relay shall be able to monitor up to four remote RTD modules, each with 12 RTD inputs, with associated over-temperature protection functions including alarm and trip settings, settable time delays, and associated outputs.  Additional functionality shall be identical to that provided by the on board RTDs as describer above.

- Protection functions associated to Power, which include alarm and trip settings, with corresponding settable time delays, and associated outputs:

  - Power Factor (55)

  - Reactive Power

  - Under Power (37)

  - Reverse Power

The relay shall operate with either wye-connected (four wire) or open-delta-connected (three wire) potential transformers, and three phase, four wire connected current transformers.

The relay shall include provisions to allow its use in conjunction with variable frequency drives.  All of the elements shall function properly with the exceptions of voltage and power elements.

The motor protection relay shall have five (5) output relays, and six (6) digital inputs.  The output relays shall be as follows: Trip Relay, Alarm Relay, two auxiliary relays, and a service relay. Five of the six digital inputs shall have the following pre-assigned default functions:

- Access Switch to allow changing of any setpoint values from the face plate,

- Differential Switch to accept inputs from an external differential protection relay

- Emergency Restart to allow a hot motor to be restarted

- External Reset, to allow resetting trips or latched alarms

- Speed Switch to accept a trip signal from a speed monitoring device

Although assigned default functions, these five inputs, along with the one remaining spare input, can be user programmable to alternate functions. The function that the input is used for may be chosen from the following list of functions: Starter Status configured for either an 'a' or 'b' auxiliary contact, Waveform Capture, Digital Counter, DeviceNet Control, and General Switch functions in which an alarm and/or trip may then be configured for that input. The relay shall be able to monitor the digital inputs of up to four remote RTD modules.

The relay shall allow motor starting and stopping via any of the communication ports. When a Stop command is sent the TRIP relay shall be activated for 1 second to complete stop sequence. When a Start command is issued, an output relay shall be assigned for starting control, which shall be activated for 1 second to complete the start sequence. The Serial Communication Control function shall also be used to reset the relay and activate a waveform capture.

The relay shall be capable of protecting the motor during the entire starting process in Reduce Voltage starting applications.

The relay shall provide complete monitoring and metering functions. These shall include:

- Current: Phasors, RMS Values of per Phase, Average, Motor Load, Current Unbalance, Unbalance Biased Motor Load, Ground, Differential Currents

- Voltage: Phasors, RMS Values of Phase-Phase and Phase-Neutral, Average Voltage

- Frequency

- Temperature of each RTD Inputs

- Motor Speed (RPM)

- Power: Power Factor, Three phase Real (kw, hp), Reactive (kvar), Apparent (kva) Power

- Energy: Watt-hours, Var-hours

- Demand: Rolling Demand method, time interval, programmed to 5 to 90 min in steps of 1 minute

- An event recorder with a record of the last 512 events, time tagged with a resolution of 10 ms.

- The waveform capture feature is similar to a transient/fault recorder. The relay shall storage of up to 16 cycles of data, captured for Phase A, B, and C currents (Ia, Ib, and Ic), Ground currents (Ig), Phase A-N, B-N, and C-N voltages (Van, Vbn, and Vcn) for wye connections, Phase A-B and B-C (Vab and Vbc) for open-delta connections

- The relay shall be able to provide data in the form of trending or data logger, sampling and recording up to eight actual values at an interval defined by the user.  Several parameters shall be trended and graphed at sampling periods ranging from 1 second up to 1 hour. The parameters which can be trended by the Setup software shall be:  Phase Currents A, B, and C, and Average Phase Current, Motor Load, Current Unbalance, Ground Current, System Frequency, Voltages Vab, Vbc, Vca Van, Vbn & Vcn, Power Factor, Real (kW or hp) Reactive (kvar), and Apparent (kVA) Power, Positive Watt-hours, Positive and Negative Var-hours, Hottest Stator RTD, Thermal Capacity Used, RTDs 1 through 12 temperature, Remote RTDs 1 through 12.

- The relay shall include four transducer outputs with a settable DC output range of 0 to 20 mA, 4 to 20 mA or 0 to 1 mA, which may be assigned to any measured parameter. The range of these outputs shall be scalable.

- The relay shall be able to monitor up to four remote RTD modules, each with four Analogue Outputs, with settable DC output range and functionality identical to the on board Analogue Outputs.  The remote RTD Module Analogue Outputs shall be assigned to any temperature measured by the module RTDs.

- Latest trip report containing date and time, cause, phase, ground, motor load, current unbalance,  Line-Line and Line-ground voltages, hottest stator RTD, system frequency, real, reactive and apparent power, and power factor

- Alarm status information reflecting Alarm Name as programmed and status.

- Start block timer status including overload lockout, start inhibit, starts per hour, time between starts, and restart block

- The relay shall provide comprehensive statistical data and learned information, as follows:

The Motor Learned Data must capture up to 250 sets of motor starting values, averaged over up to five motor starts. The motor learned data must be graphically represented through a PDF report.

The following is the learned data captured and stored and can also be printed and filed.

- Learned Acceleration Time

- Learned Starting Time

- Learned Starting Capacity

- Learned Running and Cool Time Constant

- Learned Stopped Cool Time Constant

- Learned Unbalance K Factor

- Learned Average Motor Load

- Learned Run Time After Start

- Date of last learned Date average calculation or last record

The relay must provide a high-speed data logger to capture analog signals during motor starting conditions.  A total of six individual logs (1 baseline and rolling buffer of last 5 starts), each 30 seconds long are available to record key analog quantities at a sampling rate of 200 milliseconds

The following information must be captured:

- True RMS Phase A, B and C Currents

- Phase Current Unbalance

- True RMS Ground Current

- True Phase to Phase or Phase to Ground Voltages

- Thermal Capacity Accumulated (%)

- System Frequency

- Breaker / Contactor Status

- Preventive Maintenance Information:

  - The relay shall keep count of number of trips by type

  - Number of motor starts or start attempts

  - Number of Emergency Restarts

  - Motor running hours

  - Autorestart start attempts

  - Time to autorestart

  - Digital input counters

- The relay shall have starter failure detection feature which shall produce an alarm in the event that the motor relay does not detect a starter/breaker open condition after a trip is initiated.

- The relay shall have the capability to display up to 5 user programmable text messages

- Under normal conditions, if no front panel activity is detected within a settable time, the screen shall sequentially display up to 30 default messages. Any actual value or setpoint message shall be selectable for default display

- Security / Change History Report

The relay must comply with NERC CIP security reporting requirements and provide traceability.  The relay must maintain a history of the last changes made to the configuration, including modifications to settings and firmware upgrades.  A summary history of the last ten sessions and a list the last 100 specific setting changes made must be recorded and stored in non-volatile memory.  The report must be available to be saved and printed in PDF format.

Security Setting Reports must the following information:

- Dates and times of security setting changes

- MAC address of user making setting changes

- Listing of modified changes

- How setting changes were made

  - Keypad, Front serial port, Ethernet

User interfaces shall include:

- A 40 character LCD display, and navigation keys

- Indicator LEDs on the front panel which shall provide a quick visual indication of status

- A front panel RS232 serial port that shall provide easy computer access. The communications protocol shall be Modbus RTU

- Two rear RS485 ports. The communications protocol shall be Modbus RTU

- An RS485 communications port shall be provided specifically designed to communicate to Remote RTD modules.  The relay shall be capable of communicating with up to four Remote RTD modules.  Access to the remote RTD modules for setpoints and actual values shall be achieved through the motor relay via any of the available communication ports.  The remote RTD communication port standard media shall be a three terminal port.  Optional media shall be fiber optic, with a maximum baud rate of 19.2 kBs, fiber sizes 50/125, 62.5/125, 100/140, and 200 µm, and emitter fiber type 820 nm LED, multimode.

- An optional RJ45 Ethernet port shall be provided to allow 10BaseT Ethernet connectivity to Local or Wide Area Networks.  The communications protocol shall be Modbus TCP

- An optional terminal port shall be provided to allow DeviceNet or Profibus connectivity to Local DeviceNet or Profibus Networks.

- The relay shall be capable of being set by Windows-based, Easy to use, Setup graphical terminal interface

- To make the data acquisition more efficient, the motor relay shall provide a User Definable Memory Map, which shall allow a remote computer to read up to 125 nonconsecutive data registers by using one Modbus packet.  The User Definable Memory Map shall be programmed to join any memory map address to one in the block of consecutive User Map locations, so that they can be accessed by means of these consecutive locations. The User Definable area shall have two sections:

  - A Register Index area containing 125 Actual Values or Setpoints registers

  - A Register area containing the data located at the addresses in the Register Index

A testing feature shall be included to allow testing analogue outputs and relays, without the need for external voltage and current inputs.

The relay must be capable of being programmed through a windows based software program that is capable of the following:

- The software program will operate in the following fashion

  - Request system and motor nameplate data from user through display screens.

  - Generate cautionary notes based on inputted information

  - Generate settings file

  - Review settings with user with the option to disable any configured settings that are not required

  - Provide PDF report outlining the settings that have been generated, as well as any cautionary notes required

  - Report and Settings file to be saved in user-selectable location

- The following system and protection settings will be generated based on inputted information

  - All CT, VT and Power System settings

  - All Thermal Model settings including

    - Short Circuit

    - Mechanical Jam

    - Unbalance

    - Undercurrent

    - Ground Fault

  - All Motor Start / Inhibit protections

  - Local RTD configuration, alarming and tripping

  - Under / Over Voltage

  - Under / Over frequency

  - Phase Reversal

  - Local Digital input for 52A / B contact

  - All other settings will have default values

- Include Typical Wiring Diagram based on CT / VT type

- Provide a summary of all enabled settings in a PDF format that can be saved or printed.

Motor Health Report

The Motor Health Report included with the relay will provide a detailed history of the operation and performance of the associated motor in both graphical and data format.  The following information will be provided in the Motor Health Report.  The report can either be saved to a location in a soft copy or be printed in PDF format.

The report shall be divided into seven categories and provide the following information:

- Device Summary

  - Requested Period

  - Report Created By

  - Motor Name

  - Protection Device

  - Firmware Version

  - Motor FLA

  - Rated Voltage

  - Phase Rotation

  - System Frequency

  - Motor Running Time

- Status Overview

  - Provide historical learned date of the following

  - Acceleration Time

  - Starting Current

  - Starting Capacity

  - Motor Load

  - Run Time After Start

- Trip Summary

  - Overload / Thermal

  - Current

  - Voltage / Frequency / Power

  - Miscellaneous

  - Information shall be represented both graphically and numerically

- Motor Operating History

  - The Motor Operating History will provide information extracted from the Events Record

  - Motor Start / Running

  - Manual Stop Command

  - Trip Command

  - Lockout

  - Alarm Conditions

  - Emergency Restarts

  - Information shall be represented both graphically and numerically

- Motor Starting Learned Information

  - Learned Data will be captured for every motor start

  - 250 Learned Data Records will be stored in the relay

  - Learned Acceleration Time

  - Learned Starting Current

  - Learned Starting Capacity

  - Learned Average Motor Load

  - Learned Average Run Time After Start

  - Information shall be represented both graphically and numerically

- Motor Start Data Logger

  - The Motor Start Data Logger consists of Baseline Record and 5 additional records

  - Each record shall contain 6 channels of information

  - Each channel shall contain 150 samples, sampled at 200ms intervals for a total of 30 seconds

  - Information to be included in the Motor Start Data Logger:

  - Average Current

  - Average Current Unbalance in Percent

  - Ground Current

  - Average Voltage

  - Thermal Capacity Used

  - Frequency

  - Breaker Status

  - Information shall be represented both graphically and numerically

- Motor Stopping / Tripping

  - Events that are related to the stopping or tripping of the motor

  - Overload Trip

  - Mechanical Jam

  - Short Circuit

  - Under Power

  - Current Unbalance

  - RTD Temperature

  - Ground Fault

  - Under/Over Voltage

  - Under/Over Frequency

  - Manual/Remote Stop

  - Information shall be represented both graphically and numerically

To help extend product life, and to protect the motor protection relay from hostile and harsh environments including moisture, temperature variations, salt spray, organic attack (fungus), and aggressive chemicals and vapors, the product manufacturer shall provide optional harsh environment conformal coating.  The following specifications shall be met:

- Military specifications MIL-I-46058-C, type AR, ER and UR

- UL recognized according to specification UL746C/94 for indoor and outdoor applications

- IEC68-2-60 Part 2, Method 3, 1995 Mixed Flowing Gas Testing