469 Guideform Specifications

November 27, 2005

NOTE TO SPECIFIER:

For more information on this product visit the GE Multilin Web Site from a product brochure at http://www.geindustrial.com/products/brochures/469.pdf

The motor management relay shall provide primary protection and management to medium voltage, medium to large motors.   The relay shall be equipped with the following protection functions.

- Motor Thermal Overload Model (49)

  - Include 15 standard overload curves, a custom curve feature, and a curve specifically designed for the starting of high inertia loads, when the acceleration time exceeds the safe stall time.

  - A second overload curve selection shall be provided for two-speed motors.

  - The stator protective thermal model shall combine inputs from positive and negative sequence currents and RTD winding feedback. This will then cause the model to become dynamic in nature in order to follow the loading and temperature of the motor.

  - Motor cooling time constants

  - Rotor protection during stall and acceleration. To achieve this the stall/acceleration curve shall be voltage compensated and a speed switch input shall be available.

- The relay shall detect ground faults or earth leakage currents as low as 0.25 A using a 50:0.025 Ground CT.

- The relay shall incorporate four 4 to 20 mA analog inputs to be used for tripping and alarming on any transducer input such as vibration, pressure, flow, etc.

- Use phase- and negative-sequence current heating to calculate motor thermal capacity during starting and running states

- Settable motor-stopped and motor running cooling time constants

- Phase and residual overcurrent elements (50P/50G)

- Negative sequence unbalance/ single phase biasing (46)

- Load-loss (undercurrent) (37)

- Mechanical jam (48)

- Motor stall protection

- Re-start blocking (i.e. Antibackspin protection) timer

- Starts-per-hour (66)

- Minimum-time-between-starts

- Differential protection using CT inputs (6) from both sides of the machine winding

- Voltage transformer inputs which shall be used to provide overvoltage (59), undervoltage (27), voltage phase reversal (47), overfrequency (81O) and underfrequency (81U) functions

- 12 RTD inputs with associated over-temperature protection functions including alarm and trip settings, with corresponding settable time delays, and associated outputs.  The following additional functionality shall be provided, associated to RTDs:

  - Able to configure each of the twelve RTDs as “None” or any one of four application types: “Stator”, “Bearing”, “Ambient”, or “Other”

  - RTD type shall be selectable between four different RTD types: “100 Ohm Platinum”, “120 Ohm Nickel”, “100 Ohm Nickel”, or “10 Ohm Copper”

  - The motor relay shall incorporate the RTD inputs to support the following:

    - Thermal overload model biasing

    - Temperature alarms and trips (49/38)

    - RTD open- or short-circuit alarm

  - The motor relay shall include trip voting for extra reliability in the event of RTD malfunction.  If enabled, a second RTD must also exceed the trip temperature of the RTD being checked before a trip is issued.

  - Provisions shall be included to allow the RTDs to be identified by name

- Protection functions associated to Power, which include alarm and trip settings, with corresponding settable time delays, and associated outputs:

  - Power Factor (55)

  - Reactive Power

  - Under Power (37)

  - Reverse Power

  - Over Torque

The relay shall have a drawout construction to facilitate testing, maintenance and interchange flexibility.

The relay shall operate with either wye-connected (four wire) or open-delta-connected (three wire) potential transformers, and three phase, four wire connected current transformers.

The relay shall include provisions to allow its use in conjunction with variable frequency drives.  All of the elements shall function properly with the exceptions of voltage and power elements.

The motor protection relay shall have six (6) output relays, and nine (9) digital inputs.  The output relays shall be as follows: Trip Relay, Alarm Relay, two auxiliary relays, block start relay and a service relay. Four of the five pre-assigned digital inputs shall have the following functions:

- Access Switch to allow changing of any setpoint values from the face plate,

- Test Switch to prevent statistical data from being corrupted or updated when the relay is under test.

- Emergency Restart to allow a hot motor to be restarted

- Remote Reset, to allow resetting trips or latched alarms

- A fifth digital input shall be provided for Starter Status, and may be configured for either an 'a' or 'b' auxiliary contact.

The remaining four digital inputs shall be user programmable. The function that the input is used for may be chosen from the following list of functions: Remote Alarm, Remote Trip, Load Shed Trip, Speed Switch Trip, Pressure Switch Alarm, Pressure Switch Trip, Vibration Switch Alarm, Vibration Switch Trip, Tachometer, Waveform Capture, Digital Counter, Simulation Pre-Fault, Simulation Fault, Simulation Pre-Fault to Fault, and General Switch functions in which an alarm and/or trip may then be configured for that input.

- If the Two-Speed Motor feature is enabled, one of the inputs shall be dedicated as the Two-Speed Motor Monitor.

The relay shall allow motor starting and stopping via any of the three communication ports. When a stop command is issued, the TRIP relay shall be activated for 1 second to allow for the breaker or starter to complete the tripping cycle. When a start command is issued, an auxiliary relay assigned for starting control shall be activated for 1 second to allow for the breaker/starter to complete the closing cycle.

The relay shall be capable of protecting the motor during the entire starting process in Reduce Voltage starting applications.

The relay shall provide complete monitoring and metering functions. These shall include:

- Current: Phasors, RMS Values of per Phase, Average, Motor Load, Current Unbalance, Ground, Differential Currents

- Voltage: Phasors, RMS Values of Phase-Phase and Phase-Neutral, Average Voltage

- Frequency

- Temperature of each RTD Inputs

- Motor Speed (RPM)

- Power: Power Factor, Three phase Real (kw, hp), Reactive (kvar), Apparent (kva) Power

- Energy: Watt-hours, Var-hours

- Torque (Nm)

- Demand: Rolling Demand method, time interval, programmed to 5 to 90 min in steps of 1 minute

- An event recorder with a record of the last 256 events, time tagged with a resolution of 10 ms.

- The waveform capture feature is similar to a transient/fault recorder. The relay shall storage of up to 64 cycles of data, captured for Phase A, B, and C currents (Ia, Ib, and Ic), Differential A, B, and C currents (Idiffa, Idiffb, and Idiffc), Ground currents (Ig), Phase A-N, B-N, and C-N voltages (Van, Vbn, and Vcn) for wye connections, Phase A-B and B-C (Vab and Vbc) for open-delta connections

- The relay shall be able to provide data in the form of trending or data logger, sampling and recording up to eight actual values at an interval defined by the user.  Several parameters shall be trended and graphed at sampling periods ranging from 1 second up to 1 hour. The parameters which can be trended by the Setup software shall be:  Phase Currents A, B, and C, and Average Phase Current, Motor Load, Current Unbalance, Ground Current, Differential Currents A, B, and C, System Frequency, Voltages Vab, Vbc, Vca Van, Vbn & Vcn, Power Factor, Real (kW or hp) Reactive (kvar), and Apparent (kVA) Power, Positive Watthours, Positive and Negative Varhours, Torque, Hottest Stator RTD, Thermal Capacity Used, RTDs 1 through 12 temperature, Current Demand, Power Demand (Active, Reactive & Apparent), Analog Inputs 1, 2, 3, and 4, Tachometer

- The relay shall include four 4 to 20 mA or 0 to 1 mA (as specified with order) transducer outputs that may be assigned to any measured parameter. The range of these outputs shall be scalable.

- Latest trip report containing date and time, cause, phase, ground, sensitive ground, and differential currents, motor load, current unbalance, speed, Line-Line and Line-ground voltages, hottest RTDs, system frequency, real, reactive and apparent power, power factor, and analog Inputs

- Alarm status information reflecting Alarm Name as programmed and status.

- Start block timer status including overload lockout, start inhibit, starts per hour, time between starts, and restart block

- The relay shall provide comprehensive statistical data and learned information, as follows:

- Learned Information: 
This data shall be accumulated based on the last five starts.

  - Acceleration time

  - Starting current

  - Thermal capacity required during motor starts

  - Last starting current, last acceleration time, last starting thermal capacity

  - Average motor load

  - RTD maximums for each RTD

  - Analog Inputs minimums and maximums

- Preventive Maintenance Information:

  - The relay shall keep count of number of trips by type

  - Number of motor starts or start attempts

  - Number of Emergency Restarts

  - Number of starter operations performed over time

  - Digital Counter via one of the programmable digital inputs

  - Motor running hours

  - Start per hour

  - Time between starts

- The relay shall have starter/breaker monitoring inputs for the detection of a failed circuit regardless of the starter/breaker state

- The relay shall have the capability to display up to 5 user programmable text messages

- Under normal conditions, if no front panel activity is detected within a settable time, the screen shall sequentially display up to 30 default messages. Any actual value or setpoint message shall be selectable for default display

User interfaces shall include:

- A large 40 character display, navigation keys, and a keypad

- Indicator LEDs on the front panel which shall provide a quick visual indication of status

- A front panel RS232 serial port that shall provide easy computer access. The communications protocol shall be Modbus RTU

- Two rear RS485 ports. The communications protocol shall be Modbus RTU

- An optional RJ45 Ethernet port shall be provided to allow 10BaseT Ethernet connectivity to Local or Wide Area Networks.  The communications protocol shall be Modbus TCP

- An optional terminal port shall be provided to allow DeviceNet connectivity to Local DeviceNet Networks.  The communications protocol shall be DeviceNet

- The relay shall be capable of being set by Windows-based, Easy to use, Setup graphical terminal interface

- To make the data acquisition more efficient, the motor relay shall provide a User Definable Memory Map, which shall allow a remote computer to read up to 125 nonconsecutive data registers by using one Modbus packet.  The User Definable Memory Map shall be programmed to join any memory map address to one in the block of consecutive User Map locations, so that they can be accessed by means of these consecutive locations. The User Definable area shall have two sections:

  - A Register Index area containing 125 Actual Values or Setpoints registers

  - A Register area containing the data located at the addresses in the Register Index

A powerful simulation feature shall be included to allow testing without the need for external voltage and current inputs.

To help extend product life, and to protect the motor protection relay from hostile and harsh environments including moisture, temperature variations, salt spray, organic attack (fungus), and aggressive chemicals and vapors, the product manufacturer shall provide optional harsh environment conformal coating.  The following specifications shall be met:

- Military specifications MIL-I-46058-C, type AR, ER and UR

- UL recognized according to specification UL746C/94 for indoor and outdoor applications

- IEC68-2-60 Part 2, Method 3, 1995 Mixed Flowing Gas Testing