489 Guideform Specifications

March 26, 2002

Generator management shall be provided using a relay with complete protection, metering, and monitoring functions. The relay may be applied on synchronous or induction generators of 25, 50, or 60 Hz.

The protection functions shall include:

- instantaneous overcurrent when offline (50)

- high-set overcurrent (50)

- distance (21)

- ground directional (67)

- instantaneous and definite time overcurrent for ground (50/51GN)

- stator thermal modeling and RTD (49)

- negative sequence overcurrent (46)

- bearing overtemperature (38)

- phase differential (87G)

- over and undervoltage (59/27)

- reverse power for anti-motoring (32)

- inadvertent generator energization (50/27)

- overspeed (12)

- voltage restrained phase overcurrent (51V)

- 100% stator ground protection (59GN/27TN)

- bearing vibration (39)

- voltage phase reversal (47)

- VT fuse failure detection (60FL)

- breaker failure detection (50BF)

- trip coil supervision

- sequential tripping logic

Synchronous generator protection shall include:

- overexcitation (24)

- loss of field (40 & 40Q)

- over and under frequency (81)

Monitoring and metering functions shall include:

- RMS current, negative sequence current, voltage, three phase power, temperature (via the 12 RTDs), and four analog inputs

- four analog output channels which can be configured to any measured parameter

- an event record which shall maintain a record of the last 40 events

The current and voltage inputs shall be sampled 12 times a cycle. The relay shall store these waveforms into a user definable buffer (up to 64 cycles long) in the event of a trip.

The protective relay shall include the following user interfaces:

- a 40 character LCD display, control keys and full numeric keypad located on the front panel

- LED indicators located on the front panel which shall indicate the status of the protection relay, generator, and output relays

- an RS232 port located on the front panel with a baud rate of 9600 bps

- two RS485 ports located on the rear of the unit with baud rates from 300 to 19,200 bps

- the communications ports shall allow simultaneous independent access using Modbus® RTU and DNP 3.0 protocol

- Windows® based PC software which enables setpoint programming, file storage, on-line help, and real time display of status and measured data

The protective relay shall be provided with drawout construction to facilitate testing, maintenance, and interchange flexibility.