Guideform Specification

## EPM2200 - Power Metering System

2.    	PRODUCT

2.1  	POWER METERS

- The meter shall be UL listed and CE marked.

B.	Power meter shall be designed for Multifunction Electrical Measurement on 3 phase power systems.

- Meter shall support 3 element wye, 2.5 element wye, 2 element delta, 4 wire delta systems.

- The meter shall accept universal voltage input.

- Surge withstand shall conform to IEEE C37.90.1

- The meter shall be user programmable for voltage range to any PT ratio.

- Meter shall accept a burden of up to 0.014VA/per phase at 120 Volts.

- The meter shall accept a voltage input range of up to 416 Volts Line to Neutral, and a range of up to 721 Volts Line to Line.

- Meter shall accept a current reading of up to 11 amps continuous.

- Power meter shall use a dual input method for current inputs.  Method one shall allow the CT to pass directly through the meter without any physical termination on the meter, ensuring the meter cannot be a point of failure on the CT circuit.  The second method shall provide additional termination pass-through bars, allowing the CT leads to be terminated on the meter.  The meter must support both termination methods.

    - Fault Current Withstand shall be 100 Amps for 10 seconds, 300 Amps for 3 seconds, and 500 Amps for 1 second.

    - Meter shall be programmable for current to any CT ratio.  DIP switches or other fixed ratios shall not be acceptable

    - Meter shall accept burden of 0.005VA per phase, Max at 11 Amps.

    - Meter shall begin reading at a 5mA pickup current.

    - Pass through wire gauge dimension of 0.177” / 4.5 mm shall be available.

    - All inputs and outputs shall be galvanically isolated to 2500 Volts AC.

    - The meter shall accept current inputs of class 10: (0 to 10) A, 5 Amp Nominal.

D.	The meter shall have an accuracy of +/- 0.4% or better for volts and amps, and 1.0% for power and energy functions.  The meter shall meet the accuracy requirements of IEC62053-22(0.5% Accuracy) and ANSI C12.20(0.5% Accuracy).

- The meter shall provide true RMS measurements of voltage, phase to neutral and phase to phase; current, per phase and neutral.

- The meter shall provide sampling at 400+ samples per cycle on all channels measured readings simultaneously.

- The meter shall utilize 24 bit Analog to Digital conversion.

E.	The meter shall include a three line, bright red, .56” LED display.

- The meter shall fit in both DIN 92mm and ANSI C39.1 Round cut-outs.

- The meter must display a % of Load Bar on the front panel to provide an analog feel.  The % Load bar shall have not less than 10 segments.

H.	The meter shall offer an optional independent communication port with advanced features.

- The port shall provide RS485 open communication protocol speaking Modbus ASCII/RTU through back plate.

- Baud rates shall be from 9600 baud to 57,600 baud.

- Meter shall have 8 Bit, No parity.

I.  The meter shall provide user configured fixed window or rolling window demand.  This shall allow user to set up the particular utility demand profile.

- Readings for kW, kVAR, kVA and PF shall be calculated using utility demand features.

- All other parameters shall offer max and min capability over the user selectable averaging period.

- Voltage shall provide an instantaneous max and min reading displaying the highest surge and lowest sag seen by the meter.

- The meter shall support a power supply of 90 to 265 Volts AC.

- Meter shall provide upgrade rate of 100msec for Watts, VAR and VA.  All other 
        parameters shall be 1 second.

      - The meter shall have a standard 1-year warranty.

L.  Power meter shall be able to be stored in (-20 to +70) degrees C.

- Operating temperature shall be (-10 to +60) degrees C.

- NEMA 12 faceplate rating shall be available for the power meter.

M.  Acceptable product is GE Multilin Model EPM 2200. The following options shall be available for ordering:

- EPM 2200A1 – Measures Volts and Amps

- EPM 2200B1 – Measures Volts, Amps, Power and Frequency

- EPM 2200C1 – Measures Volts, Amps, Power, Frequency, and Energy Counters

All models are available with and without the RS485 and KYZ Pulse Communications option