L60 Guideform Specifications

Firmware revision 3.00

Transmission line distance protection, control, monitoring and metering shall be supplied in one integrated digital relay package for application on transmission lines and suitable for incorporation in an integrated substation control system.

The protection system shall be available with three phase tripping logic. The relay shall be suitable for use with power line carrier communication channels with a channel test facility to determine the health of the communications channel.

# Protection Functions:

## Phase Comparison Protection

- Protection shall be provided for both single-phase comparison and dual-phase- comparison.

- Protection shall be provided for both blocking and tripping scheme applications.

- Facilities have to be provided to measure and compensate for the channel delay.

- Facilities have to be provided to adjust coincidence (stability) angle.

- Relay shall interface PLC (power line carrier) and comply with applicable standards.

- Transient blocking functionality shall be provided to cope with current reversals.

## Phase and Ground Distance Protection

- Distance characteristics for both phase and ground protection shall include: mho, lens, and quadrilateral characteristics.

- Elements shall have independent direction, shape, reach, maximum torque angle, overcurrent supervision, zero-sequence compensation, blinders and timer settings.

- All phase distance elements shall work with CTs and VTs located independently from each other at any side of a three-phase wye-delta transformer. The distance elements shall include an adaptive reach feature for application on series compensated lines. The reach shall be adjusted automatically based on the current level to provide maximum security.

- Pilot-aided permissive overreaching transfer trip (POTT) scheme shall be provided.

- Close-onto-fault protection shall be provided

## Out-of-Step Protection and Power Swing Blocking

- Integrated out-of-step tripping and power swing blocking functions shall be provided.

- The out-of-step tripping protection shall be programmable to trip either in an early (instantaneous) or delayed (when the current envelope is at the minimum) mode.

- Both out-of-step tripping and power swing blocking shall be programmable to work with 2 or 3 characteristics.

- Current supervision shall be available for both the functions.

## Load Encroachment

- Load encroachment characteristics responding to positive-sequence voltage and current shall be provided.

- Minimum voltage supervision shall be available for the function.

## Fast and Sensitive Ground Directional Protection

- The relay shall include neutral and negative-sequence directional overcurrent elements for fast and sensitive fault direction discrimination.

- The neutral and negative-Sequence elements shall include an offset impedance for faster and more reliable operation and application on series compensated lines.

- The neutral overcurrent element shall respond to neutral (internally calculated) or ground (externally supplied) current. The element shall respond to neutral (internally calculated) or auxiliary (externally supplied) polarizing voltage. The element shall be polarized from voltage, current or both.

- The negative-sequence directional element shall respond to negative-sequence direction and either negative-sequence or neutral currents.

- The neutral and negative-sequence directional elements shall include positive-sequence restraint for increased security.

- The neutral and negative-sequence directional elements shall include simultaneous forward and reverse indications.

- The neutral and negative-sequence directional elements shall be configurable for any pilot-aided scheme and for directional control of any protection element.

## Overcurrent Protection

- Eight time overcurrent elements: for phase, neutral, ground and negative-sequence currents (two TOCs for each) shall be provided.

- Time overcurrent curve characteristics: IEEE, IEC, IAC, I2t, definite time, and four custom curves for precise or difficult coordination shall be available.

- Eight instantaneous overcurrent elements: for phase, neutral, ground and negative-sequence currents (two IOCs for each) shall be available.

- Six directional overcurrent elements: for phase, neutral, ground and negative-sequence (two elements for each) shall be available.

## Voltage Protection

- Two phase under- and one over-voltage elements shall be provided

- Auxiliary under- and over-voltage elements shall be provided

- Neutral overvoltage element

- The overvoltage elements shall use time curves including user-programmable curves

## VT fuse fail detection

## Disturbance Detection

# Control Functions:

## Two Breaker Failure Elements

- The breaker fail elements shall be configurable to respond to two different currents such as in breaker-and-a-half application.

- The breaker fail elements shall respond to three levels of current in three-pole and single-pole modes as well as to breaker contacts.

## Two Synchrocheck Elements

- The synchrocheck elements shall be configurable to respond to any combination of single-phase voltages such as in breaker-and-a-half application.

- Dead source logic shall be included.

## Automatic Recloser

- Four shot, three-pole autorecloser shall be provided.

## Programmable logic including non-volatile latches

## Eight FlexElements™ for user-definable protection functions

- Flexible control of all input and output contacts shall be provided.

- All elements shall have a blocking input that allows supervision of the element from other elements, contact inputs, etc.

## Switchable Setting Groups

- The relay shall have switchable setting groups for dynamic reconfiguration of the protection elements due to changed conditions such as system configuration changes, or seasonal requirements.

# Monitoring and Metering Functions:

## Fault location and reporting.

- Voltage (phasors, true RMS values, symmetrical components), current (phasors, symmetrical components, true RMS values), real, reactive and apparent power, power factor and frequency.

- Breaker Arcing Current (I 2t)

- The relay shall calculate an estimate of the per phase wear on the breaker contacts by measuring and integrating the current squared passing through the breaker contact as an arc.

## User-programmable oscillography

## User-programmable data logger

## Trip circuit monitoring

UR Common Guideform Specifications

Firmware revision 3.00

The relay shall be provided in one integrated package suitable for incorporation in an integrated substation control system. The relay shall be housed in a horizontal, 4 RU, 19-inch rack chassis configuration. It shall be a modular design to easily facilitate upgrading or repair by replacement of modules. The faceplate interface shall include an alphanumeric vacuum fluorescent display, keypad, and LED target indicators.

The logic that determines the interaction of inputs, features, and outputs shall be re-configurable through the use of FlexLogic™ equations. The use of remote inputs and outputs in addition to hardware shall be available on the communications ports using the UCA2 GOOSE (Generic Object Oriented Substation Event) mechanism to minimize the requirement for auxiliary components and wiring. The contact inputs shall accept wet or dry contacts. Contact outputs shall be trip rated Form-A with current and voltage circuit monitors, Form-C, or Fast Form-C for signaling. Hardware input/output capability shall be expandable.

The relay shall have three communications ports that operate independently and simultaneously. The RS232 port shall be accessible from the faceplate of the relay. The second port shall be RS485 supporting ModBus® RTU and DNP 3.0 protocols capable of baud rates up to 115 kbps. The third communications port shall be either a similar RS485 port or a 10 Mbps Ethernet port supporting MMS/UCA2, ModBus®/TCP, and DNP 3.0 or IEC 60870 protocols. The physical port shall be 10BaseF, or redundant 10BaseF.

The relay shall be supplied with supporting application software for use on a PC with Windows® 95/98/NT operating systems. The program shall be capable of retrieving Comtrade oscillography files from the relay to display, save, or print when troubleshooting. The software shall provide the capability of editing and managing settings files to store to the relay or disk backup, while on-line or off-line. The software shall also permit the updating of new relay firmware and viewing of all trip and alarm target messages, and the 1024 time stamped events recorded by the relay.

The relay clock shall be capable of being synchronized with an IRIG-B signal to allow synchronism with other connected devices. The relay shall allow for SNTP network-based time synchronization.