MM200 Guideform Specifications

October 2008

NOTE TO SPECIFIER:

For more information on this product visit the GE Multilin Web Site for a product brochure and instruction manual at

http://www.gedigitalenergy.com/multilin/brochure/mm200.htm

http://www.gedigitalenergy.com/multilin/manuals/mm200.htm

The motor management relay shall provide primary protection and management to low voltage motors rated 690 Volts and below.   The relay shall be equipped with the following protection functions.

- Motor Thermal Overload Model (49)

  - The Thermal Model shall consist of the following:

  - Include 15 standard overload curves

  - Hot/cold biasing that accounts for normal temperature rise.

  - Cooling rate that accounts for heat dissipation

  - Thermal protection reset that controls recovery from thermal trips and lockouts.

- The relay shall detect ground faults or earth leakage currents as low as 0.50 A using a 50:0.025 Ground CT.

- Use phase current heating to calculate motor thermal capacity during starting and running states

- Settable motor stopped and motor running cooling time constants

- Ground Instantaneous overcurrent elements (50G)

- Unbalance / single phase biasing (46)

- Load-loss (undercurrent) (37)

- Ground time overcurrent (51G)

- Locked/stalled rotor, mechanical jam (51R)

- Motor stall protection

- The relay shall be equipped with an acceleration timer

- The relay shall be equipped with a load increase alarm

- The relay shall have a thermistor input.

- The relays shall have internal Current Transformers (C.T.’s) rated and 1A/5A and shall be suitable for direct connection up to 5A FLA.

- The relay power supply shall be rated at 24VDC or an AC power supply rated at 60 – 300VAC

- The relays shall be capable of operating with 50Hz and 60 Hz systems

- The relay shall have programmed starter logic and shall support the following starter types.  Full Voltage Non-Reversing (FVNR), Full Voltage Reversing (FVR), Two Speed.

  - Inputs and Outputs shall be automatically assigned based on the starter type.

- The relay shall be capable of being DIN rail mounted.

- Digital Inputs

  - The relay shall have two (2) Form A and one (1) Form C outputs.

  - The relay shall have seven (7) digital inputs rated at 24VDC.

  - Or

  - The relay shall have two (2) Form A and one (1) Form C outputs.

  - The relay shall have six (6) digital inputs rated at 65 to 300 VAC.

- The relay shall be suitable to operate in temperatures from –20 degrees Celsius to +60 degrees Celsius with up to 90% non-condensing humidity.

The relay shall provide complete monitoring and metering functions. These shall include:

- Current: RMS Values of per Phase, Average Current, Ground Current, Motor Load, Current Unbalance, Thermal Capacity

- The relay shall provide the following information:

  - Total number of trips

  - Overload trips

  - Mechanical jam trips

  - Undercurrent trips

  - Current Unbalance trips

  - Ground fault trips

  - Motor acceleration trips

- The relay shall capture the number of motor starts and motor running hours.

- The following learned data shall be provided:

  - Learned acceleration time

  - Learned starting current

  - Learned starting capacity

  - Learned average motor load

User interfaces shall include:

- A control panel shall be available with the relay

- The control panel shall include the following:

  - Start A, Start B and Stop pushbuttons

  - Auto/Manual/Reset pushbuttons

  - LED indicators:

    - Running, Stopped, Tripped, Alarm, Comms OK, Auto, Manual

    - Motor load 50%, 80%, 100%

    - User Programmable designated as, User 1 and User 2.

    - LED color indication shall change based on condition

- The relay shall be capable of being set by Windows-based, Easy to use, Setup graphical terminal interface

- Communications

- The relay shall have one RS485 port. The communications protocol shall be Modbus RTU.  Baud rate for RS485 shall be from 9600 to 115200 baud.

- An optional terminal port shall be provided to allow DeviceNet (125, 250 or 500 kps) or Profibus connectivity to Local DeviceNet or Profibus Networks.

- The relay shall be capable of communicating through all communication protocols simultaneously and without the use of protocol converters.

- The relay shall be capable of being programmed by a Windows-based, Easy to use, Setup graphical terminal interface

- Approvals

- The relay shall be manufactured under an ISO9001 registered program

- The relay shall be cUL Listed

- The relay shall conform to EN 60255-26 (EN 50263), EN 5502 / CISPR22 / EN61000-6-2

- The relay shall conform to UL 508 / UL 1053 and C22.2.14.05 (CSA)